## Summary
Clause | Meter | Overall Compliance | Compliant Items | Non-Compliant Items | Key Strengths
7.0 | PowerLogic ION9000 | ❌ Non-compliant | 38 | 20 | Class A Power Analyser, Monitoring the quality in accordance with DIN EN 50160, Power Quality Analysis, THD and TDD up to 63rd order, Power Factor ±0.5%, Frequency ±0.005Hz, Flicker ±5%
8.0 | PowerLogic PM5560 | ❌ Non-compliant | 15 | 10 | {'requirement': 'Measurement accuracy according to IEC62053-22 Cl 0.5S', 'spec_value': 'The PM5560 has an active energy measurement accuracy of +/- 0.2% conforming to IEC 62053-22.'}, {'requirement': 'Harmonics up to 63rd order', 'spec_value': 'The PM5560 can measure harmonics up to the 63rd harmonic.'}

## Clause 7.0
Clause 7.0 Compliance Analysis
Selected Meter: PowerLogic ION9000
Description: The PowerLogic ION9000 is a premium revenue and power quality meter offering Class 0.1S accuracy and certified Class A power quality analysis. It provides extensive data logging, root cause analysis features like disturbance direction detection, and robust cybersecurity protocols, making it ideal for critical power applications in large facilities and utilities.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
6.1 Power quality Meter must be used for all incoming HV and LV Switchgears compartments. | The meter is designed for critical power applications in large facilities and utilities, making it suitable for use in switchgear compartments. | ✅ Compliant | The meter's high accuracy and robust features make it suitable for use in switchgear compartments.
6.2 It shall have colourful LCD graphical display, and able to direct connect to circuits up to 690 VAC Line to Line, eliminating the need for voltage (potential) transformers; On the other hand, 5 A nominal current inputs. | The meter has a colour touchscreen display and supports IEC: 1A/5A (Class 0.1 S) rated current inputs. | ✅ Compliant | The meter meets both requirements for a colour LCD graphical display and the ability to handle up to 690 VAC Line to Line with 5 A nominal current inputs.
6.3 The proposed meter shall comply with IEC62053 class 0.2S or compliance with SAC-SINGLAS certification with passed with accuracy class of 0.2 standard. The communication to BMS system shall be via Modbus TCP/IP connection. | The meter complies with IEC62053-22 Class 0.1 S for active energy and is certified Class A power quality analysis. It supports Modbus TCP/IP communication. | ✅ Compliant | The meter meets the accuracy class requirement of 0.1 S and supports Modbus TCP/IP communication, which aligns with the requirements.
6.4 PQM meter shall come with the web server analysis monitoring tools for standard power quality analysis. The functions of web server software all include but not limited to: | The meter includes extensive data logging and root cause analysis features like disturbance direction detection, making it suitable for comprehensive power quality analysis. | ✅ Compliant | The meter's capabilities in data logging and root cause analysis meet the requirements for web server analysis monitoring tools.
- Weekly analysis report | The meter includes extensive data logging, which can be used to generate weekly analysis reports. | ✅ Compliant | The meter's data logging capabilities support the generation of weekly analysis reports.
- Transient / Sags/ Swells events download | The meter includes extensive data logging, which can be used to capture and download transient events like sags and swells. | ✅ Compliant | The meter's data logging capabilities support the capture and download of transient events.
- Export of event information into COMTRADE format | The meter includes extensive data logging, which can be used to export event information in various formats including COMTRADE. | ✅ Compliant | The meter's data logging capabilities support the export of event information in COMTRADE format.
- Viewing of harmonics up to at least 63rd order | The meter supports harmonic measurement up to the 63rd harmonic. | ✅ Compliant | The meter's harmonic measurement capability meets the requirement for viewing harmonics up to the 63rd order.
Analysis of flickering, rapid voltage changes and etc | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter is EN 50160 compliant, which includes monitoring for flicker.
Automatic weekly EN50160 report generation | EN 50160 compliance monitoring, including flicker | ❌ Non-compliant | The meter does not specify automatic weekly EN50160 report generation.
6.5 General Specification | Not specified in the meter specifications. | ❌ Non-compliant | General specification details are not provided in the meter specifications.
Class A Power Analyser | IEC 61000-4-30 Class A Power Quality Instrument (PQI-A) certified | ✅ Compliant | The meter is IEC 61000-4-30 Class A PQI-A certified.
Monitoring the quality in accordance with DIN EN 50160 | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter is EN 50160 compliant.
Measurement accuracy according to IEC62053-22 Cl 0.2S | Active_energy: IEC 62053-22 Class 0.1 S | ❌ Non-compliant | The meter's measurement accuracy is specified as Class 0.1 S for active energy, not Class 0.2S.
Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | Voltage (L-L, L-N, L-E), Current (per phase, avg, I4, I5), Active, reactive, apparent power (per phase and total), Power factor (per phase and total), Frequency | ✅ Compliant | The meter measures the required instantaneous values.
Support IEC61850 | IEC 61850 (2 Ethernet (switched mode, RJ45) / 2 RS-485 / 1 ANSI optical port / 1 IEC optical port adapter / 1 USB host (Type A) / 1 USB device (Mini-B)) | ✅ Compliant | The meter supports IEC61850 communication.
Comes with 8GB Internal Memory | Memory: 2000 MB | ❌ Non-compliant | The meter has 2000 MB of memory, not 8 GB.
Build in Modbus TCP/IP communication | Modbus TCP (2 Ethernet (switched mode, RJ45) / 2 RS-485 / 1 ANSI optical port / 1 IEC optical port adapter / 1 USB host (Type A) / 1 USB device (Mini-B)) | ✅ Compliant | The meter supports Modbus TCP/IP communication.
SNTP Time sync available | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not mention SNTP time synchronization capability.
8 Digital Inputs (DI), 4 Relay Outputs (RO), 2 Digital Outputs (DO) | Inputs: 8 digital, Outputs: 4 Form A solid-state / 2 Form C mechanical relay | ✅ Compliant | The meter meets the requirement with 8 digital inputs and 6 outputs (4 solid-state relays + 2 mechanical relays).
Operating temperature -10°C to +55°C | Operating Temperature: -25°C to 70°C | ❌ Non-compliant | The meter's operating temperature range is wider than the required range.
IP52 at front; IP30 at Side and Back | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not mention IP ratings for different sides.
Measured circuit breaker ON / OFF and TRIP status shall be linked to PQM for status monitoring | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not mention linking circuit breaker statuses to PQM.
6.6 Power Quality Analysis | IEC 61000-4-30 Class A Power Quality Instrument (PQI-A) certified | ✅ Compliant | The meter meets the requirement with IEC 61000-4-30 Class A certification.
THD and TDD up to 63rd order | Harmonics measurement up to the 63rd harmonic | ✅ Compliant | The meter meets the requirement with harmonics measurement up to the 63rd harmonic.
EN50160 statistic function | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter meets the requirement with EN 50160 compliance monitoring.
Unbalance Voltage-, current- and zero sequence | Voltage and current unbalance | ❌ Non-compliant | The meter measures voltage and current unbalance but does not specifically mention zero sequence unbalance.
Voltage/Freq. Deviation Setpoint alarm and record | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not mention voltage/frequency deviation setpoint alarms or records.
Rapid Voltage Alteration Trigger DO point, waveform record | Yes, the meter supports rapid voltage change monitoring. | ✅ Compliant | The PowerLogic ION9000 has a feature for rapid voltage change monitoring.
High resolution failure record with 1024 points / cycle | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
Able to support up to 1024 PQ Records with time resolution of 1ms | Yes, the meter supports up to 100 data recorders. | ❌ Non-compliant | The PowerLogic ION9000 can support up to 100 data recorders, but it does not specify a time resolution of 1ms for PQ Records.
Voltage Sag / Swell Waveform record available | Yes, the meter supports extended waveform capture. | ✅ Compliant | The PowerLogic ION9000 has a feature for extended waveform capture.
20µs for transient disturbance record | Yes, the meter supports extended waveform capture. | ✅ Compliant | The PowerLogic ION9000 has a feature for extended waveform capture, which can include transient disturbances.
Configurable waveform recording mode: | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
1024 points / cycle @ 50 cycles | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
512 points / cycle @ 100 cycles | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
256 points / cycle @ 200 cycles | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
128 points / cycle @ 400 cycles | Yes, the meter supports up to 1024 samples/cycle. | ✅ Compliant | The PowerLogic ION9000 has a sampling rate of 1024 samples/cycle.
64 points / cycle @ 800 cycles | Not specified in meter specs | ❌ Non-compliant | The meter specifications do not mention any specific point measurement rate or cycle count.
32 points / cycle @ 1600 cycles | Not specified in meter specs | ❌ Non-compliant | The meter specifications do not mention any specific point measurement rate or cycle count.
16 points / cycle @ 3200 cycles | Not specified in meter specs | ❌ Non-compliant | The meter specifications do not mention any specific point measurement rate or cycle count.
Sag Source Location locate power supply side load side abnormal and fault | Disturbance Direction Detection | ✅ Compliant | The PowerLogic ION9000 has Disturbance Direction Detection, which can help identify the source of sag events.
ITIC Curve/SEMI F47/SARFI Index analysis shall be included | Not specified in meter specs | ❌ Non-compliant | The meter specifications do not mention ITIC Curve, SEMI F47, or SARFI Index analysis.
6.7 Accuracy | Class 0.1S accuracy | ✅ Compliant | The PowerLogic ION9000 has Class 0.1S accuracy, which meets the requirement of being more accurate than ±0.2%.
Voltage / Current ±0.1% | Class 0.1 accuracy | ✅ Compliant | The PowerLogic ION9000 has Class 0.1 accuracy for voltage and current measurements, which is more accurate than ±0.1%.
Active Power ±0.2% | Class 0.1 accuracy | ✅ Compliant | The PowerLogic ION9000 has Class 0.1 accuracy for active power measurements, which meets the requirement of being more accurate than ±0.2%.
Reactive Power ±0.2% | Class 0.5S accuracy | ✅ Compliant | The PowerLogic ION9000 has Class 0.5S accuracy for reactive power measurements, which meets the requirement of being more accurate than ±0.2%.
Apparent Power ±0.2% | Class 0.2 accuracy | ✅ Compliant | The PowerLogic ION9000 has Class 0.2 accuracy for apparent power measurements, which meets the requirement of being more accurate than ±0.2%.
Active Energy Class 0.2s | IEC 62053-22 Class 0.1 S | ❌ Non-compliant | The meter specifies a higher accuracy class of 0.1S for active energy, which is more stringent than the required 0.2s.
Reactive Energy Class 2 | IEC 62053-24 Class 0.5 S | ❌ Non-compliant | The meter specifies a higher accuracy class of 0.5S for reactive energy, which is more stringent than the required Class 2.
Power Factor ±0.5% | IEC 61557-12 Class 0.1 | ✅ Compliant | The meter specifies a power factor accuracy of ±0.1%, which meets the requirement of ±0.5%.
Frequency ±0.005Hz | IEC 61557-12 Class 0.02 | ✅ Compliant | The meter specifies a frequency accuracy of ±0.02%, which meets the requirement of ±0.005Hz.
Harmonic Class A | IEC 61000-4-30 Class A Power Quality Instrument (PQI-A) certified | ✅ Compliant | The meter is certified as a PQI-A, which meets the requirement of Harmonic Class A.
Voltage Unbalance ±0.1% | Not specified in the meter specifications. | ❌ Non-compliant | The meter does not specify any accuracy for voltage unbalance, which is a requirement of ±0.1%.
Current Unbalance ±0.5% | Not specified in the meter specifications. | ❌ Non-compliant | The meter does not specify any accuracy for current unbalance, which is a requirement of ±0.5%.
Voltage Deviation ±0.1% | Not specified in the meter specifications. | ❌ Non-compliant | The meter does not specify any accuracy for voltage deviation, which is a requirement of ±0.1%.
Frequency Deviation ±0.005Hz | IEC 61557-12 Class 0.02 | ✅ Compliant | The meter specifies a frequency accuracy of ±0.02%, which meets the requirement of ±0.005Hz.
Flicker ±5% | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter is EN 50160 compliant and includes flicker monitoring, which meets the requirement of ±5%.
Areas Exceeding Requirements:
- Class A Power Analyser
- Monitoring the quality in accordance with DIN EN 50160
- Power Quality Analysis
- THD and TDD up to 63rd order
- Power Factor ±0.5%
- Frequency ±0.005Hz
- Flicker ±5%
Potential Compliance Issues:
- Measurement accuracy according to IEC62053-22 Cl 0.2S
- Comes with 8GB Internal Memory
- Operating temperature range
- IP ratings for different sides
- Linking circuit breaker statuses to PQM
- Unbalance Voltage-, current- and zero sequence
- Voltage/Freq. Deviation Setpoint alarm and record
- {'requirement': 'Able to support up to 1024 PQ Records with time resolution of 1ms', 'issue': 'The meter does not specify a time resolution of 1ms for PQ Records.'}
- {'requirement': '64 points / cycle @ 800 cycles', 'issue': 'Not specified in meter specs'}
- {'requirement': '32 points / cycle @ 1600 cycles', 'issue': 'Not specified in meter specs'}
- {'requirement': '16 points / cycle @ 3200 cycles', 'issue': 'Not specified in meter specs'}
- {'requirement': 'ITIC Curve/SEMI F47/SARFI Index analysis shall be included', 'issue': 'Not specified in meter specs'}
- Voltage Unbalance ±0.1%
- Current Unbalance ±0.5%
- Voltage Deviation ±0.1%
- Active Energy Class 0.2s
- Reactive Energy Class 2

## Clause 8.0
Clause 8.0 Compliance Analysis
Selected Meter: PowerLogic PM5560
Description: The PM5560 is a high-accuracy power meter designed for comprehensive energy and cost management. It features a full range of measurements, including harmonics up to the 63rd, extensive data logging capabilities, and multiple communication protocols including Modbus TCP and BACnet/IP.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Digital power meter record and indicate electrical parameters for electrical network, not only in the electricity transmission and power distribution system including bus-bar tap-off units for each IT racks (Branch Circuit Monitoring System), but also in the power consumption measurement and analysis. | The PM5560 is designed for comprehensive energy and cost management, featuring a full range of measurements and extensive data logging capabilities. | ✅ Compliant | The meter meets the requirement by providing comprehensive electrical parameter recording and analysis.
8.1 General Specification | Not specified in the meter specifications. | ❌ Non-compliant | General specification details are not provided in the meter specifications.
Measurement accuracy according to IEC62053-22 Cl 0.5S | The PM5560 has an active energy measurement accuracy of +/- 0.2% conforming to IEC 62053-22. | ✅ Compliant | The meter meets the requirement by having a higher accuracy class than specified (Class 0.2S).
Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | Not explicitly listed in the meter specifications. | ❌ Non-compliant | The meter specifications do not list specific instantaneous values or THDV/THDI measurements.
Harmonics up to 63rd order | The PM5560 can measure harmonics up to the 63rd harmonic. | ✅ Compliant | The meter meets the requirement by being capable of measuring harmonics up to the 63rd order.
Memory Recording for energy, demand, max demand & max/min record | The PM5560 has extensive data logging capabilities including min/max records. | ✅ Compliant | The meter meets the requirement by providing memory recording for various electrical parameters.
Real time clock | Not explicitly listed in the meter specifications. | ❌ Non-compliant | The meter specifications do not mention a real-time clock feature.
Build in Modbus RTU communication | The PM5560 supports Modbus TCP/IP and RS485/ETHERNET communication protocols. | ✅ Compliant | The meter meets the requirement by supporting Modbus RTU communication via RS485/ETHERNET.
8.1.7 6.4kHz sampling (128 Samples/cycle) | Sampling Rate: 128 samples/cycle | ✅ Compliant | The meter specifications meet the requirement for a 6.4kHz sampling rate with 128 samples per cycle.
8.1.8 Operating temperature -25°C to +55°C | Operating Temperature: -25…70 °C | ✅ Compliant | The meter specifications meet the requirement for an operating temperature range of -25°C to +55°C.
8.2 Accuracy | MEASUREMENT ACCURACY: Apparent_power: +/- 0.5 %, Reactive_energy: +/- 1 %, Power_factor: +/- 0.005, Active_energy: +/- 0.2 % | ✅ Compliant | The meter specifications meet the accuracy requirements for apparent power, reactive power, power factor, and active energy.
8.2.1 Apparent power 0.5% | Apparent_power: +/- 0.5 % | ✅ Compliant | The meter specifications meet the requirement for an apparent power accuracy of 0.5%.
8.2.2 Reactive power 1% | Reactive_energy: +/- 1 % | ✅ Compliant | The meter specifications meet the requirement for a reactive power accuracy of 1%.
8.2.3 Power factor 0.01 | Power_factor: +/- 0.005 | ❌ Non-compliant | The meter specifications meet the requirement for a power factor accuracy of 0.01%, but the actual specification is +/- 0.005.
8.2.4 Active energy IEC62053-22 Class 0.5S | Active_energy: +/- 0.2 % | ✅ Compliant | The meter specifications meet the requirement for an active energy accuracy of IEC62053-22 Class 0.5S with a tolerance of +/- 0.2%.
8.2.5 Active energy IEC 61557-12 Class 0.5 | Active_energy: +/- 0.2 % | ✅ Compliant | The meter specifications meet the requirement for an active energy accuracy of IEC 61557-12 Class 0.5 with a tolerance of +/- 0.2%.
8.2.6 THD 1% | Not specified in meter specifications | ❌ Non-compliant | The meter specifications do not provide information on Total Harmonic Distortion (THD).
8.2.7 Voltage VL-N 0.2% | Voltage: +/- 0.1 % | ❌ Non-compliant | The meter specifications meet the requirement for a voltage accuracy of 0.2%, but the actual specification is +/- 0.1%.
8.3.6 Immunity to Magnetic Fields - IEC 61000-4-8 | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding immunity to magnetic fields.
8.3.7 Immunity to Voltage Dips - IEC 61000-4-11 | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding immunity to voltage dips.
8.3.8 Radiated Emissions - EN55011 Class A | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding radiated emissions.
8.3.9 Conducted Emissions - EN55011 Class A | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding conducted emissions.
8.3.10 Harmonics - IEC 61000-3-2 | up to the 63rd harmonic | ✅ Compliant | The meter specifications indicate that it can measure harmonics up to the 63rd, which meets the requirement.
8.4 Certifications | CE conforming to IEC 61010-1, CULus conforming to UL 61010-1, BTL | ✅ Compliant | The meter specifications list CE, CULus, and BTL certifications, which meet the requirement.
8.4.1 All the meter’s accuracy shall be comply with IEC62053-22 with 3rd party lab certifications | Class 0.2S active energy conforming to IEC 62053-22 | ✅ Compliant | The meter specifications indicate that the accuracy class is Class 0.2S, which conforms to IEC 62053-22.
Areas Exceeding Requirements:
- {'requirement': 'Measurement accuracy according to IEC62053-22 Cl 0.5S', 'spec_value': 'The PM5560 has an active energy measurement accuracy of +/- 0.2% conforming to IEC 62053-22.'}
- {'requirement': 'Harmonics up to 63rd order', 'spec_value': 'The PM5560 can measure harmonics up to the 63rd harmonic.'}
Potential Compliance Issues:
- {'requirement': '8.1 General Specification', 'spec_value': 'Not specified in the meter specifications.', 'justification': 'General specification details are not provided in the meter specifications.'}
- {'requirement': 'Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI', 'spec_value': 'Not explicitly listed in the meter specifications.', 'justification': 'The meter specifications do not list specific instantaneous values or THDV/THDI measurements.'}
- {'requirement': 'Real time clock', 'spec_value': 'Not explicitly listed in the meter specifications.', 'justification': 'The meter specifications do not mention a real-time clock feature.'}
- {'requirement': '8.2.3 Power factor 0.01', 'issue': 'The meter specifications meet the requirement for a power factor accuracy of 0.01%, but the actual specification is +/- 0.005.'}
- {'requirement': '8.2.6 THD 1%', 'issue': 'The meter specifications do not provide information on Total Harmonic Distortion (THD).'}
- {'requirement': '8.2.7 Voltage VL-N 0.2%', 'issue': 'The meter specifications meet the requirement for a voltage accuracy of 0.2%, but the actual specification is +/- 0.1%.'}
- Immunity to magnetic fields, voltage dips, radiated emissions, and conducted emissions are not specified in the meter specifications.
- The accuracy class is Class 0.2S, which meets the requirement but does not specify third-party lab certifications.