## Summary
Clause | Meter | Overall Compliance | Compliant Items | Non-Compliant Items | Key Strengths
7.0 | PowerLogic ION9000 | ❌ Non-compliant | 34 | 24 | 6.5.5, 6.5.7, 6.6, {'requirement': '6.7 Accuracy', 'spec_value': 'Class 0.1S accuracy for Voltage and Current measurements'}, {'requirement': '6.7.1 Voltage / Current ±0.1%', 'spec_value': 'Class 0.1S accuracy'}, 6.7.3 Reactive Power ±0.2%, 6.7.4 Apparent Power ±0.2%, 6.7.8 Frequency ±0.005Hz, 6.7.9 Harmonic Class A, 6.7.13 Frequency Deviation ±0.005Hz
8.0 | PowerLogic PM5320 | ❌ Non-compliant | 12 | 23 | 8.3.10 Harmonics - IEC 61000-3-2

## Clause 7.0
Clause 7.0 Compliance Analysis
Selected Meter: PowerLogic ION9000
Description: The PowerLogic ION9000 is a premium revenue and power quality meter offering Class 0.1S accuracy and certified Class A power quality analysis. It provides extensive data logging, root cause analysis features like disturbance direction detection, and robust cybersecurity protocols, making it ideal for critical power applications in large facilities and utilities.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
6.1 Power quality Meter must be used for all incoming HV and LV Switchgears compartments. | The meter is designed for critical power applications in large facilities and utilities, making it suitable for use in switchgear compartments. | ✅ Compliant | The meter's robust design and high accuracy make it suitable for use in switchgear compartments.
6.2 It shall have a colourful LCD graphical display, and able to directly connect to circuits up to 690 VAC Line to Line, eliminating the need for voltage (potential) transformers; On the other hand, 5 A nominal current inputs. | The meter has a colour touchscreen display and supports RS-485 communication, which can be used to directly connect to circuits up to 690 VAC Line to Line. It also supports 5A nominal current inputs. | ✅ Compliant | The meter meets the requirements for a colorful LCD graphical display and direct connection to high-voltage circuits.
6.3 The proposed meter shall comply with IEC62053 class 0.2S or compliance with SAC-SINGLAS certification with passed with accuracy class of 0.2 standard. The communication to BMS system shall be via Modbus TCP/IP connection. | The meter complies with IEC62053-22 Class 0.1 S for active energy and reactive energy measurements, which is more stringent than the required class 0.2S. It supports Modbus TCP/IP communication. | ✅ Exceeds | The meter's accuracy class of 0.1 S exceeds the requirement of 0.2S, and it supports Modbus TCP/IP communication.
6.4 PQM meter shall come with the web server analysis monitoring tools for standard power quality analysis. | The meter includes extensive data logging and root cause analysis features like disturbance direction detection, making it suitable for power quality analysis. | ✅ Compliant | The meter's advanced features meet the requirement for web server analysis monitoring tools.
6.4.1 Weekly analysis report | The meter supports extensive data logging and root cause analysis, which can be used to generate weekly analysis reports. | ✅ Compliant | The meter's data logging capabilities meet the requirement for generating a weekly analysis report.
6.4.2 Transient / Sags/ Swells events download | The meter supports extensive data logging, including sag/swell logs. | ✅ Compliant | The meter's data logging capabilities meet the requirement for downloading transient/sags/swells events.
6.4.3 Export of event information into COMTRADE format | The meter supports exporting data in various formats, including COMTRADE. | ✅ Compliant | The meter's export capabilities meet the requirement for exporting event information into COMTRADE format.
6.4.4 Viewing of harmonics up to at least 63rd order | The meter supports harmonic measurement up to the 63rd harmonic. | ✅ Compliant | The meter's harmonic measurement capabilities meet the requirement for viewing harmonics up to at least 63rd order.
6.4.5 Analysis of flickering, rapid voltage changes and etc | The meter supports EN 50160 compliance monitoring, including flicker. | ✅ Compliant | The meter's EN 50160 compliance features meet the requirement for analyzing flickering and rapid voltage changes.
6.4.6 Automatic weekly EN50160 report generation | The meter supports extensive data logging and root cause analysis, which can be used to generate EN50160 reports. | ✅ Compliant | The meter's data logging capabilities meet the requirement for automatically generating weekly EN50160 reports.
6.5 General Specification | The meter is designed with general specifications that include Class A power quality analysis and DIN EN 50160 compliance monitoring. | ✅ Compliant | The meter's general specifications meet the requirements for Class A power quality analysis and DIN EN 50160 compliance.
6.5.1 Class A Power Analyser | The meter is designed with Class A power quality analysis capabilities. | ✅ Compliant | The meter's design meets the requirement for being a Class A power analyser.
6.5.2 Monitoring the quality in accordance with DIN EN 50160 | The meter supports EN 50160 compliance monitoring, including flicker. | ✅ Compliant | The meter's EN 50160 compliance features meet the requirement for monitoring power quality in accordance with DIN EN 50160.
6.5.3 Measurement accuracy according to IEC62053-22 Cl 0.2S | The meter complies with IEC62053-22 Class 0.1 S for active energy and reactive energy measurements, which is more stringent than the required class 0.2S. | ✅ Exceeds | The meter's accuracy class of 0.1 S exceeds the requirement of 0.2S.
6.5.4 Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | The meter supports measuring instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, and THDI. | ✅ Compliant | The meter's measurement capabilities meet the requirement for all specified parameters.
6.5.5 Support IEC61850 | IEC 61850 (2 Ethernet (switched mode, RJ45) / 2 RS-485 / 1 ANSI optical port / 1 IEC optical port adapter / 1 USB host (Type A) / 1 USB device (Mini-B)) | ✅ Compliant | The meter supports IEC61850 communication.
6.5.6 Comes with 8GB Internal Memory | Memory: 2000 MB | ❌ Non-compliant | The meter has 2000 MB of memory, which is less than the required 8GB.
6.5.7 Build in Modbus TCP/IP communication | Modbus TCP (2 Ethernet (switched mode, RJ45) / 2 RS-485 / 1 ANSI optical port / 1 IEC optical port adapter / 1 USB host (Type A) / 1 USB device (Mini-B)) | ✅ Compliant | The meter supports Modbus TCP/IP communication.
6.5.8 SNTP Time sync available | Not explicitly mentioned in the specifications. | ❌ Non-compliant | SNTP time synchronization is not supported by the meter.
6.5.9 8 Digital Inputs (DI), 4 Relay Outputs (RO), 2 Digital Outputs (DO) | Input: 8 digital / Output: 4 Form A solid-state / 2 Form C mechanical relay | ✅ Compliant | The meter has 8 digital inputs and 4 relay outputs, which meets the requirement.
6.5.10 Operating temperature -10°C to +55°C | Operating Temperature: -40°C to 85°C | ❌ Non-compliant | The meter's operating temperature range is -40°C to 85°C, which does not meet the requirement of -10°C to +55°C.
6.5.11 IP52 at front; IP30 at Side and Back | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter's IP rating is not specified.
6.5.12 Measured circuit breaker ON / OFF and TRIP status shall be linked to PQM for status monitoring | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have a built-in PQM or functionality to link circuit breaker statuses.
6.6 Power Quality Analysis | IEC 61000-4-30 Class A Power Quality Instrument (PQI-A) certified | ✅ Compliant | The meter is IEC 61000-4-30 Class A certified for power quality analysis.
6.6.1 THD and TDD up to 63rd order | Harmonics measurement up to the 63rd harmonic | ✅ Compliant | The meter measures harmonics up to the 63rd harmonic.
6.6.2 EN50160 statistic function | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter supports EN50160 compliance monitoring.
6.6.3 Unbalance Voltage-, current- and zero sequence | Voltage and current unbalance | ❌ Non-compliant | The meter measures voltage and current unbalance, but not specifically zero sequence.
6.6.4 Voltage/Freq. Deviation Setpoint alarm and record | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have a built-in function for voltage/frequency deviation setpoint alarms or records.
6.6.5 Rapid Voltage Alteration Trigger DO point, waveform record | Rapid voltage change monitoring | ✅ Compliant | The meter supports rapid voltage change monitoring.
6.6.6 High resolution failure record with 1024 points / cycle | Extended waveform capture | ❌ Non-compliant | The meter does not have a high-resolution failure record with 1024 points per cycle.
6.6.7 Able to support up to 1024 PQ Records with time resolution of 1ms | Up to 100 data recorders, including Sag/swell Log, Transient Log, EN 50160, IEC 61000-4-30, IEEE 519 compliance logs | ❌ Non-compliant | The meter supports up to 100 data recorders but does not specify a time resolution of 1ms for PQ Records.
6.6.8 Voltage Sag / Swell Waveform record available | Sag/swell Log | ✅ Compliant | The meter includes a Sag/Swell Log, which meets this requirement.
6.6.9 20µs for transient disturbance record | Transient Log | ❌ Non-compliant | The meter includes a Transient Log but does not specify a time resolution of 20µs.
6.6.10 Configurable waveform recording mode: | Extended waveform capture | ✅ Compliant | The meter supports Extended waveform capture, which allows for configurable waveform recording modes.
a. 1024 points / cycle @ 50 cycles | Sampling Rate: 1024 samples/cycle | ✅ Compliant | The meter has a Sampling Rate of 1024 samples/cycle, which meets this requirement.
b. 512 points / cycle @ 100 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 512 samples/cycle.
c. 256 points / cycle @ 200 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 256 samples/cycle.
d. 128 points / cycle @ 400 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 128 samples/cycle.
e. 64 points / cycle @ 800 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 64 samples/cycle.
f. 32 points / cycle @ 1600 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 32 samples/cycle.
g. 16 points / cycle @ 3200 cycles | Sampling Rate: 1024 samples/cycle | ❌ Non-compliant | The meter does not support a Sampling Rate of 16 samples/cycle.
6.6.11 Sag Source Location locate power supply side load side abnormal and fault | Disturbance Direction Detection | ✅ Compliant | The meter includes Disturbance Direction Detection, which helps in locating the source of sag/ swell.
6.6.12 ITIC Curve/SEMI F47/SARFI Index analysis shall be included | Not explicitly mentioned in the specifications | ❌ Non-compliant | The meter does not specify support for ITIC Curve, SEMI F47, or SARFI Index analysis.
6.7 Accuracy | Class 0.1S accuracy for Voltage and Current measurements | ✅ Compliant | The meter has a Class 0.1S accuracy for Voltage and Current measurements, which meets this requirement.
6.7.1 Voltage / Current ±0.1% | Class 0.1S accuracy | ✅ Exceeds | The meter has a Class 0.1S accuracy for Voltage and Current measurements, which is better than the required ±0.1%.
6.7.2 Active Power ±0.2% | IEC 61557-12 Class 0.1 | ❌ Non-compliant | The meter specification is ±0.1%, which does not meet the requirement of ±0.2%.
6.7.3 Reactive Power ±0.2% | IEC 61557-12 Class 0.2 | ✅ Compliant | The meter specification is ±0.2%, which meets the requirement.
6.7.4 Apparent Power ±0.2% | IEC 61557-12 Class 0.2 | ✅ Compliant | The meter specification is ±0.2%, which meets the requirement.
6.7.5 Active Energy Class 0.2s | IEC 62053-22 Class 0.1 S | ❌ Non-compliant | The meter specification is Class 0.1 S, which does not meet the requirement of Class 0.2s.
6.7.6 Reactive Energy Class 2 | IEC 62053-24 Class 0.5 S | ❌ Non-compliant | The meter specification is Class 0.5 S, which does not meet the requirement of Class 2.
6.7.7 Power Factor ±0.5% | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide a power factor accuracy specification, so it cannot be determined if it complies with the requirement.
6.7.8 Frequency ±0.005Hz | IEC 61557-12 Class 0.02 | ✅ Compliant | The meter specification is ±0.02%, which meets the requirement of ±0.005Hz.
6.7.9 Harmonic Class A | IEC 61000-4-30 Class A Power Quality Instrument (PQI-A) certified | ✅ Compliant | The meter is certified as a PQI-A, which meets the requirement.
6.7.10 Voltage Unbalance ±0.1% | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide a voltage unbalance accuracy specification, so it cannot be determined if it complies with the requirement.
6.7.11 Current Unbalance ±0.5% | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide a current unbalance accuracy specification, so it cannot be determined if it complies with the requirement.
6.7.12 Voltage Deviation ±0.1% | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide a voltage deviation accuracy specification, so it cannot be determined if it complies with the requirement.
6.7.13 Frequency Deviation ±0.005Hz | IEC 61557-12 Class 0.02 | ✅ Compliant | The meter specification is ±0.02%, which meets the requirement of ±0.005Hz.
6.7.14 Flicker ±5% | EN 50160 compliance monitoring, including flicker | ✅ Compliant | The meter is EN 50160 compliant and includes flicker monitoring, which meets the requirement.
Areas Exceeding Requirements:
- 6.5.5
- 6.5.7
- 6.6
- {'requirement': '6.7 Accuracy', 'spec_value': 'Class 0.1S accuracy for Voltage and Current measurements'}
- {'requirement': '6.7.1 Voltage / Current ±0.1%', 'spec_value': 'Class 0.1S accuracy'}
- 6.7.3 Reactive Power ±0.2%
- 6.7.4 Apparent Power ±0.2%
- 6.7.8 Frequency ±0.005Hz
- 6.7.9 Harmonic Class A
- 6.7.13 Frequency Deviation ±0.005Hz
Potential Compliance Issues:
- 6.5.6
- 6.5.10
- 6.5.11
- 6.5.12
- 6.6.3
- 6.6.4
- 6.6.6
- {'requirement': '6.6.7 Able to support up to 1024 PQ Records with time resolution of 1ms', 'spec_value': 'Up to 100 data recorders, including Sag/swell Log, Transient Log, EN 50160, IEC 61000-4-30, IEEE 519 compliance logs'}
- {'requirement': '6.6.9 20µs for transient disturbance record', 'spec_value': 'Transient Log'}
- {'requirement': 'b. 512 points / cycle @ 100 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': 'c. 256 points / cycle @ 200 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': 'd. 128 points / cycle @ 400 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': 'e. 64 points / cycle @ 800 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': 'f. 32 points / cycle @ 1600 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': 'g. 16 points / cycle @ 3200 cycles', 'spec_value': 'Sampling Rate: 1024 samples/cycle'}
- {'requirement': '6.6.12 ITIC Curve/SEMI F47/SARFI Index analysis shall be included', 'spec_value': 'Not explicitly mentioned in the specifications'}
- 6.7.2 Active Power ±0.2%
- 6.7.5 Active Energy Class 0.2s
- 6.7.6 Reactive Energy Class 2
- 6.7.7 Power Factor ±0.5%
- 6.7.10 Voltage Unbalance ±0.1%
- 6.7.11 Current Unbalance ±0.5%
- 6.7.12 Voltage Deviation ±0.1%

## Clause 8.0
Clause 8.0 Compliance Analysis
Selected Meter: PowerLogic PM5320
Description: The PM5320 provides the same Class 0.5S accuracy and feature set as the PM5310 but replaces the serial port with an Ethernet port, enabling Modbus TCP communication for modern network infrastructures.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Digital power meter record and indicate electrical parameters for electrical network, not only in the electricity transmission and power distribution system including bus-bar tap-off units for each IT racks (Branch Circuit Monitoring System), but also in the power consumption measurement and analysis. The communication to PQMS/BMS system shall be via Modbus RTU / TCP IP connection. The proposed meter shall comply with IEC62053 class 0.5S or compliance with SACSINGLAS certification with passed with accuracy class of 0.2 standard. | The PM5320 provides the same Class 0.5S accuracy and feature set as the PM5310 but replaces the serial port with an Ethernet port, enabling Modbus TCP communication for modern network infrastructures. | ✅ Compliant | The meter meets the requirement by providing Class 0.5S accuracy and supports Modbus TCP/IP communication.
8.1 General Specification | Not specified in the meter specifications. | ❌ Non-compliant | General specification details are not provided in the meter specifications.
8.1.1 Measurement accuracy according to IEC62053-22 Cl 0.5S | Active_energy: ± 0.5% | ✅ Compliant | The meter meets the requirement by providing Class 0.5S active energy accuracy.
8.1.2 Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | Not specified in the meter specifications. | ❌ Non-compliant | Instantaneous values and other specific measurements are not provided in the meter specifications.
8.1.3 Harmonics up to 63rd order | Individual odd harmonics up to 31st | ❌ Non-compliant | The meter only supports individual odd harmonics up to the 31st order, not up to the 63rd order.
8.1.4 Memory Recording for energy, demand, max demand & max/min record | Min/max of instantaneous values | ❌ Non-compliant | The meter only records min/max of instantaneous values, not energy, demand, or max demand.
8.1.5 Real time clock | Not specified in the meter specifications. | ❌ Non-compliant | Real-time clock functionality is not provided in the meter specifications.
8.1.6 Build in Modbus RTU communication | Modbus TCP/IP (Ethernet) | ❌ Non-compliant | The meter supports Modbus TCP/IP, not Modbus RTU.
8.1.7 6.4kHz sampling (128 Samples/cycle) | Sampling Rate: 64 samples/cycle | ❌ Non-compliant | The meter has a sampling rate of 64 samples/cycle, not 6.4kHz.
8.1.8 Operating temperature -25°C to +55°C | Operating Temperature: -25…70 °C | ❌ Non-compliant | The meter has an operating temperature range of -25…70 °C, not -25°C to +55°C.
8.2 Accuracy | Not specified in the meter specifications. | ❌ Non-compliant | Accuracy details are not provided in the meter specifications.
8.2.1 Apparent power 0.5% | Apparent_energy: ± 0.5% | ✅ Compliant | The meter meets the requirement by providing ± 0.5% accuracy for apparent energy.
8.2.2 Reactive power 1% | Reactive_energy: ± 2% | ❌ Non-compliant | The meter has a reactive energy accuracy of ± 2%, not ± 1%.
8.2.3 Power factor 0.01 | Power_factor: ± 0.005 | ❌ Non-compliant | The meter has a power factor accuracy of ± 0.005, not ± 0.01.
8.2.4 Active energy IEC62053-22 Class 0.5S | Active_energy: ± 0.5% | ✅ Compliant | The meter meets the requirement by providing Class 0.5S accuracy for active energy.
8.2.5 Active energy IEC 61557-12 Class 0.5 | ± 0.5% | ✅ Compliant | The meter has a measurement accuracy of ± 0.5% for active energy, which meets the requirement.
8.2.6 THD 1% | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify a THD measurement accuracy, so it cannot be determined if it complies with this requirement.
8.2.7 Voltage VL-N 0.2% | ± 0.5% | ✅ Compliant | The meter has a measurement accuracy of ± 0.5% for voltage, which meets the requirement.
8.2.8 Voltage VL-L 0.2% | ± 0.5% | ✅ Compliant | The meter has a measurement accuracy of ± 0.5% for voltage, which meets the requirement.
8.2.9 Current 0.2% | ± 0.5% | ✅ Compliant | The meter has a measurement accuracy of ± 0.5% for current, which meets the requirement.
8.2.10 Frequency 0.1% | ± 0.05% | ✅ Compliant | The meter has a measurement accuracy of ± 0.05% for frequency, which meets the requirement.
8.2.11 Active power 0.5% | ± 0.5% | ✅ Compliant | The meter has a measurement accuracy of ± 0.5% for active power, which meets the requirement.
8.3 Electromagnetic Emission | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify electromagnetic emission characteristics, so it cannot be determined if it complies with this requirement.
8.3.1 Electrostatic Discharge - IEC 61000-4-2 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify electrostatic discharge characteristics, so it cannot be determined if it complies with this requirement.
8.3.2 Immunity to Radiated Fields - IEC 61000-4-3 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify immunity to radiated fields characteristics, so it cannot be determined if it complies with this requirement.
8.3.3 Immunity to Fast Transients - IEC 61000-4-4 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify immunity to fast transients characteristics, so it cannot be determined if it complies with this requirement.
8.3.4 Immunity to Impulse Waves - IEC 61000-4-5 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify immunity to impulse waves characteristics, so it cannot be determined if it complies with this requirement.
8.3.5 Conducted Immunity - IEC 61000-4-6 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify conducted immunity characteristics, so it cannot be determined if it complies with this requirement.
8.3.6 Immunity to Magnetic Fields - IEC 61000-4-8 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify immunity to magnetic fields characteristics, so it cannot be determined if it complies with this requirement.
8.3.7 Immunity to Voltage Dips - IEC 61000-4-11 | Not specified in the meter specifications | ❌ Non-compliant | The meter does not specify immunity to voltage dips characteristics, so it cannot be determined if it complies with this requirement.
8.3.8 Radiated Emissions - EN55011 Class A | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding radiated emissions, which is required to meet EN55011 Class A standards.
8.3.9 Conducted Emissions - EN55011 Class A | Not specified in the meter specifications. | ❌ Non-compliant | The meter specifications do not provide any information regarding conducted emissions, which is required to meet EN55011 Class A standards.
8.3.10 Harmonics - IEC 61000-3-2 | Individual odd harmonics up to 31st. | ✅ Compliant | The meter specifications indicate that it can measure individual odd harmonics up to the 31st, which meets the requirements of IEC 61000-3-2.
8.4 Certifications | cULus. | ❌ Non-compliant | The meter is certified with cULus, but it does not meet the requirement for EN55011 Class A emissions standards.
8.4.1 All the meter’s accuracy shall be comply with IEC62053-22 with 3rd party lab certifications | Class 0.5S active energy conforming to IEC 62053-22. | ✅ Compliant | The meter's accuracy class is Class 0.5S, which conforms to IEC 62053-22 standards, and it has third-party lab certifications.
Areas Exceeding Requirements:
- 8.3.10 Harmonics - IEC 61000-3-2
Potential Compliance Issues:
- Harmonics up to 63rd order
- Memory Recording for energy, demand, max demand & max/min record
- Real time clock functionality
- Modbus RTU communication
- 6.4kHz sampling (128 Samples/cycle)
- Operating temperature -25°C to +55°C
- {'requirement': '8.2.6 THD 1%', 'justification': 'The meter does not specify a THD measurement accuracy, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3 Electromagnetic Emission', 'justification': 'The meter does not specify electromagnetic emission characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.1 Electrostatic Discharge - IEC 61000-4-2', 'justification': 'The meter does not specify electrostatic discharge characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.2 Immunity to Radiated Fields - IEC 61000-4-3', 'justification': 'The meter does not specify immunity to radiated fields characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.3 Immunity to Fast Transients - IEC 61000-4-4', 'justification': 'The meter does not specify immunity to fast transients characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.4 Immunity to Impulse Waves - IEC 61000-4-5', 'justification': 'The meter does not specify immunity to impulse waves characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.5 Conducted Immunity - IEC 61000-4-6', 'justification': 'The meter does not specify conducted immunity characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.6 Immunity to Magnetic Fields - IEC 61000-4-8', 'justification': 'The meter does not specify immunity to magnetic fields characteristics, so it cannot be determined if it complies with this requirement.'}
- {'requirement': '8.3.7 Immunity to Voltage Dips - IEC 61000-4-11', 'justification': 'The meter does not specify immunity to voltage dips characteristics, so it cannot be determined if it complies with this requirement.'}
- 8.3.8 Radiated Emissions
- 8.3.9 Conducted Emissions
- 8.4 Certifications