## Summary
Clause | Meter | Overall Compliance | Compliant Items | Non-Compliant Items | Key Strengths
7.0 | ION9000 | ❌ Non-compliant | 0 | 39
8.0 | PM5560 | ❌ Non-compliant | 4 | 22 | Measurement accuracy, Voltage accuracy

## Clause 7.0
Clause 7.0 Compliance Analysis
Selected Meter: ION9000
Description: From PM5000_Series
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Power quality Meter must be used for all incoming HV and LV Switchgears compartments | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention its use in specific switchgear compartments.
Colourful LCD graphical display with ability to direct connect to circuits up to 690 VAC Line to Line, eliminating the need for voltage transformers; 5 A nominal current inputs | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention its display capabilities or voltage/current input ranges.
Complies with IEC 62053 class 0.2S or SAC-SINGLAS certification with passed accuracy class of 0.2 standard | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention any certifications or accuracy classes.
Communication via Modbus TCP/IP connection | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention communication interfaces.
Web server analysis monitoring tools including weekly analysis report, transient/sags/swells events download, export into COMTRADE format, viewing harmonics up to at least 63rd order, flickering analysis, automatic EN50160 report generation | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention any web server or specific monitoring tools.
Class A Power Analyser | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention power analyser capabilities.
Monitoring quality in accordance with DIN EN 50160 | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention compliance with DIN EN 50160.
Measurement accuracy according to IEC 62053-22 Cl 0.2S | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention measurement accuracy.
Support for IEC 61850 | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention support for IEC 61850.
8GB Internal Memory | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention internal memory capacity.
SNTP Time sync available | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention time synchronization capabilities.
8 Digital Inputs (DI), 4 Relay Outputs (RO), 2 Digital Outputs (DO) | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention digital input/output capabilities.
Operating temperature -10°C to +55°C | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention operating temperature range.
IP52 at front; IP30 at Side and Back | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention IP ratings.
Measured circuit breaker ON/OFF/TRIP status linked for status monitoring | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention circuit breaker status monitoring capabilities.
THD and TDD up to 63rd order | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention THD/TDD measurement capabilities.
EN50160 statistic function | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention EN50160 statistics.
Unbalance Voltage-, current- and zero sequence | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention unbalance measurement capabilities.
Voltage/Freq. Deviation Setpoint alarm and record | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention deviation setpoint alarms or records.
Rapid Voltage Alteration Trigger DO point, waveform record | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention rapid voltage alteration triggers or waveforms.
High resolution failure record with 1024 points / cycle | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention high resolution failure records.
Support for up to 1024 PQ Records with time resolution of 1ms | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention PQ record support.
Voltage Sag/Swell Waveform record available | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention voltage sag/swell waveform records.
20µs for transient disturbance record | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention transient disturbance records.
Configurable waveform recording mode: 50 cycles, 100 cycles, 200 cycles, 400 cycles, 800 cycles, 1600 cycles, 3200 cycles | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention configurable waveform recording modes.
Sag Source Location locate power supply side load side abnormal and fault | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention sag source location capabilities.
ITIC Curve/SEMI F47/SARFI Index analysis included | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention ITIC curve or SEMI F47/SARFI index analysis.
Voltage Accuracy ±0.1% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention voltage accuracy.
Current Accuracy ±0.1% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention current accuracy.
Frequency Accuracy ±0.005Hz | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention frequency accuracy.
Active Power Accuracy ±0.2% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention active power accuracy.
Active Energy Class 0.2s | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention active energy class.
Reactive Energy Class 2 | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention reactive energy class.
Power Factor Accuracy ±0.5% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention power factor accuracy.
Voltage Unbalance ±0.1% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention voltage unbalance.
Current Unbalance ±0.5% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention current unbalance.
Voltage Deviation ±0.1% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention voltage deviation.
Frequency Deviation ±0.005Hz | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention frequency deviation.
Flicker ±5% | Not specified in the meter specifications | ❌ Non-compliant | The meter specifications do not mention flicker measurement capabilities.
Potential Compliance Issues:
- No specific certification for revenue metering mentioned

## Clause 8.0
Clause 8.0 Compliance Analysis
Selected Meter: PM5560
Description: Standard power quality meter with integrated display, 512 MB memory, and 256 samples/cycle.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Measurement accuracy according to IEC62053-22 Cl 0.5S | Class 0.5 S (±1%) | ✅ Exceeds | The meter's Class 0.5 S (±1%) EXCEEDS the required IEC62053-22 Cl 0.5S accuracy
Instantaneous values (L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI) | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention support for instantaneous values.
Harmonics up to 63rd order | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention support for harmonics up to 63rd order.
Memory recording for energy, demand, max demand & max/min record | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention memory recording capabilities.
Real-time clock | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention a real-time clock feature.
Built-in Modbus RTU communication | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention built-in Modbus RTU communication capability.
Sampling rate: 6.4kHz (128 Samples/cycle) | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention a sampling rate of 6.4kHz.
Operating temperature range: -25°C to +55°C | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention an operating temperature range of -25°C to +55°C.
Apparent power accuracy: ±0.5% | Class 0.5 S (±1%) | ✅ Exceeds | The meter's Class 0.5 S (±1%) EXCEEDS the required ±0.5% apparent power accuracy
Reactive power accuracy: ±1% | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention reactive power accuracy.
Power factor accuracy: ±0.01 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention power factor accuracy.
Active energy IEC62053-22 Class 0.5S | Class 0.5 S (±1%) | ✅ Exceeds | The meter's Class 0.5 S (±1%) EXCEEDS the required IEC62053-22 Class 0.5S accuracy
Active energy IEC 61557-12 Class 0.5 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention active energy accuracy according to IEC 61557-12 Class 0.5.
Total harmonic distortion (THD) accuracy: ±1% | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention THD accuracy.
Voltage accuracy: VL-N ±0.2%, VL-L ±0.2% | Class 0.5 S (±1%) | ✅ Exceeds | The meter's Class 0.5 S (±1%) EXCEEDS the required ±0.2% voltage accuracy
Current accuracy: ±0.2% | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention current accuracy.
Frequency accuracy: ±0.1% | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention frequency accuracy.
Electrostatic Discharge immunity IEC 61000-4-2 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention electrostatic discharge immunity.
Immunity to radiated fields IEC 61000-4-3 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention immunity to radiated fields.
Immunity to fast transients IEC 61000-4-4 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention immunity to fast transients.
Immunity to impulse waves IEC 61000-4-5 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention immunity to impulse waves.
Conducted immunity IEC 61000-4-6 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention conducted immunity.
Immunity to magnetic fields IEC 61000-4-8 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention immunity to magnetic fields.
Immunity to voltage dips IEC 61000-4-11 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention immunity to voltage dips.
Radiated emissions EN55011 Class A | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention radiated emissions.
Harmonics compliance with IEC 61000-3-2 | Not specified in meter data | ❌ Non-compliant | The meter specifications do not mention harmonics compliance.
Areas Exceeding Requirements:
- Measurement accuracy
- Voltage accuracy
Potential Compliance Issues:
- No specific certification for revenue metering mentioned