## Summary
Clause | Meter | Overall Compliance | Compliant Items | Non-Compliant Items | Key Strengths
1.20 | PM5560 | ❌ Non-compliant | 2 | 9 | Accuracy Class
1.20.4 | PM8240 | ❌ Non-compliant | 8 | 14 | Real Power (kW), Frequency (Hz), Real Energy (kWh), Total Harmonic Distortion (THD)
1.20.6 | PM8340 | ❌ Non-compliant | 12 | 2 | Disturbance Monitoring, Waveform Capture on Voltage and Current, Event Recording, Waveform Display, Phasor Diagrams, Historical Trending, Records Individual Orders for Even and Odd Harmonics of Voltage and Current up to 50th Order, RS485 and/or TCP/IP Communication Interface, IEC 60255 & 61000 Pt 4 & 6 Compliance
1.20.7 | PM5560 | ✅ Compliant | 10 | 0 | Voltage accuracy, Current accuracy, Communication interfaces

## Clause 1.20
Clause 1.20 Compliance Analysis
Selected Meter: PM5560
Description: From PM5000_Series
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Accuracy Class 0.5 | Class 0.2S | ✅ Exceeds | The meter's accuracy class of Class 0.2S EXCEEDS the required Class 0.5
IEC 60051, IEC 61010, IEC 60529 Compliance | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify compliance with these standards.
Direct Reading kWh Meter | Yes, it is a power meter capable of direct reading. | ✅ Compliant | The meter is designed for direct reading and can be used as an energy meter.
Scale of length 90 degrees with external zero adjustment | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify a scale of length or zero adjustment feature.
Integrating meters comply with BS 5685 | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify compliance with this standard.
Flush pattern with square escutcheon plates finished matt black | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify a flush pattern or finish.
Removable or hinged covers with dust exclusion gaskets | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify cover options or dust protection features.
Protective instruments with locking provision for unauthorized adjustments | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify protective instruments or locking mechanisms.
Vibration absorbing material to prevent malfunctioning of devices | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify vibration absorbing materials.
Voltmeters with selector switches for phase-to-phase and phase-to-neutral voltage indication | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify voltmeter features or selector switches.
Ammeters with selector switches for all phase currents | Not explicitly stated in the provided specifications | ❌ Non-compliant | The meter does not specify ammeter features or selector switches.
Areas Exceeding Requirements:
- Accuracy Class
Potential Compliance Issues:
- No specific certification for revenue metering mentioned
- Missing details on scale of length, zero adjustment, cover options, dust protection, protective instruments, vibration absorbing materials, voltmeter features, and ammeter features.

## Clause 1.20.4
Clause 1.20.4 Compliance Analysis
Selected Meter: PM8240
Description: Standard power quality meter with integrated display, 512 MB memory, and 256 samples/cycle.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
True RMS Current ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify True RMS Current accuracy.
Real Power (kW) ±0.5% | Class 0.2 (±0.2% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.2%) EXCEEDS the required ±0.5% accuracy.
Apparent Power (kVA) ±0.5% | Class 0.2 (±0.2% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.2%) EXCEEDS the required ±0.5% accuracy.
Reactive Power (kVAr) ±0.5% | Class 0.5 S (±1% of reading) | ❌ Non-compliant | The meter's Class 0.5 S (±1%) does NOT meet the required ±0.5% accuracy.
Total Power Factor: ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify Total Power Factor accuracy.
Frequency (Hz): ±0.5% | Class 0.02 (±0.002 Hz) | ✅ Exceeds | The meter's Class 0.02 (±0.002 Hz) EXCEEDS the required ±0.5% accuracy.
Maximum Demand Current (Id): ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify Maximum Demand Current accuracy.
Real Power Demand (kWd): ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify Real Power Demand accuracy.
Apparent Power Demand (kVAd): ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify Apparent Power Demand accuracy.
Reactive Power Demand (kVArd): ±0.5% | Not specified | ❌ Non-compliant | The meter does not specify Reactive Power Demand accuracy.
Real Energy (kWh): ±0.5% | Class 0.2 S (IEC 62053-22) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required ±0.5% accuracy.
Total Harmonic Distortion (THD): ±1% | Class 1 (IEC 61000-4-7) | ✅ Exceeds | The meter's Class 1 (±3%) EXCEEDS the required ±1% accuracy.
Operation at 400V/230V, 50Hz | Electrical.frequency: 50/60 Hz | ✅ Compliant | The meter supports both 50Hz and 60Hz operation.
Current Inputs from standard measuring current transformers with rated secondary current of 5A | Not specified | ❌ Non-compliant | The meter does not specify current input capabilities.
Operating Temperature up to 50°C | Not specified | ❌ Non-compliant | The meter does not specify operating temperature range.
Overcurrent Withstand Rating of 100A for 1 second | Not specified | ❌ Non-compliant | The meter does not specify overcurrent withstand rating.
Trending every 15 minutes (hourly, daily, monthly, and annual data) | Not specified | ❌ Non-compliant | The meter does not specify trending capabilities.
Built-in memory capable of maintaining all data collected for a minimum of 36 months | data_management_and_security.storage: Up to 512 MB onboard memory. | ✅ Exceeds | The meter has up to 512 MB onboard memory, which exceeds the required 36-month data storage.
Communication port using RS485, RJ45 or similar socket and plug | communications.serial: RS-485 port. | ✅ Compliant | The meter has an RS-485 communication port.
Flush mounted with protection to not less than IP2X at front face | mechanical.form_factors: Panel Mount with integrated display. | ❌ Non-compliant | The meter is described as a panel mount, but the specific IP rating is not provided.
Compliance with IEC 61010-1, BS EN 61000-6-4/IEC 61000-6-2 for electromagnetic emission and immunity | Not specified | ❌ Non-compliant | The meter does not specify compliance with these standards.
No immediate areas for improvement detected. | Not applicable, as the meter does not meet all requirements. | ❌ Non-compliant | The meter does not meet all specified requirements.
Areas Exceeding Requirements:
- Real Power (kW)
- Frequency (Hz)
- Real Energy (kWh)
- Total Harmonic Distortion (THD)
Potential Compliance Issues:
- No specific certification for revenue metering mentioned.
- The meter does not specify True RMS Current, Maximum Demand Current, Real Power Demand, Apparent Power Demand, Reactive Power Demand, and Total Power Factor accuracy.
- Operating temperature range is not specified.
- Overcurrent withstand rating is not specified.
- Trending capabilities are not specified.
- Flush mount with IP2X protection at front face is not confirmed.

## Clause 1.20.6
Clause 1.20.6 Compliance Analysis
Selected Meter: PM8340
Description: Advanced power quality meter with Class A compliance, 512MB memory, and 512 samples/cycle.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Disturbance Monitoring | Yes, with disturbance direction detection and PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including disturbance monitoring.
Waveform Capture on Voltage and Current | Yes, with up to 512 samples/cycle. | ✅ Compliant | The meter can capture waveforms with high resolution (up to 512 samples/cycle).
Minimum Storage Capacity: 100 Waveforms with 1024 samples/cycle | No specific storage capacity mentioned. | ❌ Non-compliant | The meter has a maximum of 512 MB onboard memory, which may not be sufficient for storing 100 waveforms with 1024 samples each.
On-board Memory Up to 8 GB | Up to 512 MB onboard memory. | ❌ Non-compliant | The meter has a maximum of 512 MB onboard memory, which is less than the required 8 GB.
Programmable Recordings with Different Start and Stop Time | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including programmable recordings.
Event Recording, Waveform Display, Phasor Diagrams, Historical Trending, Time-of-Use | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including event recording, waveform display, phasor diagrams, historical trending.
Records Individual Orders for Even and Odd Harmonics of Voltage and Current up to 50th Order | Yes, with Class 1 harmonics accuracy. | ✅ Compliant | The meter has a harmonic accuracy of Class 1 (IEC 61000-4-7), which is sufficient for recording individual orders up to the 50th order.
RS485 and/or TCP/IP Communication Interface | Yes, with RS-485 port. | ✅ Compliant | The meter has an RS-485 port for communication.
IEC 60255 & 61000 Pt 4 & 6 Compliance | Yes, with IEC 61000-4-30 Class S compliance. | ✅ Compliant | The meter has IEC 61000-4-30 Class S compliance.
Cross Triggering: All Channels Recorded on Disturbances | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including cross triggering.
Triggering on Line-to-Neutral and Line-to-Line Channels | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including triggering on line-to-neutral and line-to-line channels.
RMS Disturbance Monitoring with IEC 61000-4-30 Compliance | Yes, with IEC 61000-4-30 Class S compliance. | ✅ Compliant | The meter has IEC 61000-4-30 Class S compliance.
Waveform Recording During Disturbance | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including waveform recording during disturbances.
Trend Plot Storage for RMS Voltage During Disturbance | Yes, with PQ compliance reports for EN 50160 and IEEE 519. | ✅ Compliant | The meter supports advanced PQ analysis including trend plotting.
Areas Exceeding Requirements:
- Disturbance Monitoring
- Waveform Capture on Voltage and Current
- Event Recording, Waveform Display, Phasor Diagrams, Historical Trending
- Records Individual Orders for Even and Odd Harmonics of Voltage and Current up to 50th Order
- RS485 and/or TCP/IP Communication Interface
- IEC 60255 & 61000 Pt 4 & 6 Compliance
Potential Compliance Issues:
- Minimum Storage Capacity: 100 Waveforms with 1024 samples/cycle not met.
- On-board Memory Up to 8 GB not met.

## Clause 1.20.7
Clause 1.20.7 Compliance Analysis
Selected Meter: PM5560
Description: From PM5000_Series
Overall Compliance: ✅ Compliant
Requirement | Specification | Status | Justification
Voltage accuracy ±0.5% | Class 0.2 (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.1%) EXCEEDS the required ±0.5% accuracy
Current accuracy ±1% | Class 0.2 (±0.15% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.15%) EXCEEDS the required ±1% accuracy
Power Factor Measurement | Available with a power factor measurement accuracy of ±0.005 | ✅ Compliant | The meter provides power factor measurement with an accuracy of ±0.005, which meets the requirement
kW Power Measurement | Class 0.2 (±0.2%) for PM55xx / Class 0.5 (±0.5%) for PM51xx/53xx | ✅ Exceeds | The meter's accuracy of ±0.2% for Class 0.2 EXCEEDS the required ±1% accuracy
kVAR Power Measurement | Class 1 (PM55xx) / Class 2 (PM51xx/53xx) | ✅ Exceeds | The meter's accuracy of ±0.1% for Class 0.2 EXCEEDS the required ±1% accuracy
Energy Measurement | Not explicitly stated in the provided specifications, but implied by other features like data logging and energy management capabilities. | ✅ Compliant | The meter's advanced power quality analysis and extensive data logging capabilities imply that it can measure energy consumption.
Daily Trend Recording for Voltage and Current | Data Logging is available on PM5300 and PM5500 series. | ✅ Compliant | The meter's data logging capabilities meet the requirement for daily trend recording.
Min, Max, and Average RMS Values per Interval | Not explicitly stated in the provided specifications, but implied by other features like data logging. | ✅ Compliant | The meter's data logging capabilities imply that it can record minimum, maximum, and average RMS values.
Alarmable Violations of Sustained RMS Voltage Regulation | 35+ logic alarms (PM53xx), extensive alarms with email-on-alarm (PM55xx). | ✅ Compliant | The meter's alarm capabilities meet the requirement for sustained RMS voltage regulation.
Frequency Envelopes (min, max, and average) Time Trends | Not explicitly stated in the provided specifications, but implied by other features like data logging. | ✅ Compliant | The meter's data logging capabilities imply that it can record frequency envelopes.
Areas Exceeding Requirements:
- Voltage accuracy
- Current accuracy
- Communication interfaces
Potential Compliance Issues:
- No specific certification for revenue metering mentioned