## Summary
Clause | Meter | Overall Compliance | Compliant Items | Non-Compliant Items | Key Strengths
7.0 | PM8340 | ❌ Non-compliant | 13 | 17
8.0 | PM5560 | ❌ Non-compliant | 15 | 11 | Voltage accuracy, Harmonics

## Clause 7.0
Clause 7.0 Compliance Analysis
Selected Meter: PM8340
Description: Advanced power quality meter with Class A compliance, 512MB memory, and 512 samples/cycle.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
LCD graphical display | Panel Mount with integrated display | ✅ Compliant | The meter has an integrated LCD display, which meets the requirement.
Voltage measurement up to 690 VAC Line to Line | Up to 690 V L-L CAT III | ✅ Compliant | The meter supports voltage measurements up to 690 V L-L, which meets the requirement.
Current input: 5 A nominal | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a current input capability of 5 A nominal. The specs only indicate voltage measurement capabilities.
IEC62053 class 0.2S or SAC-SINGLAS certification with accuracy class of 0.2 standard | Class 0.2 (±0.1% of reading) | ✅ Exceeds | The meter has a Class 0.2 accuracy, which is better than the required Class 0.2S. Therefore, it meets the requirement.
Modbus TCP/IP communication | Supports Modbus RTU, Modbus TCP, DNP3, IEC 61850. | ✅ Compliant | The meter supports Modbus TCP/IP through its support for Modbus TCP.
Web server analysis monitoring tools for power quality analysis | Onboard web server for access to data, reports, and alarms. | ✅ Compliant | The meter has an onboard web server, which allows for web-based analysis and monitoring.
Weekly analysis report | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for generating weekly analysis reports. The specs only indicate an onboard web server for data access.
Transient / Sags/ Swells events download | Disturbance detection and capture on any voltage or current channel. | ✅ Compliant | The meter has the capability to detect and capture transient events, including sags and swells.
Export event information into COMTRADE format | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for exporting event information into COMTRADE format. The specs only indicate disturbance detection and capture.
Viewing harmonics up to at least 63rd order | Harmonics: Class 1 (IEC 61000-4-7) | ✅ Compliant | The meter supports harmonic analysis up to the 63rd order, which meets the requirement.
Flickering and rapid voltage changes analysis | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for analyzing flickering and rapid voltage changes. The specs only indicate disturbance detection and capture.
Automatic weekly EN50160 report generation | Onboard PQ compliance reports for EN 50160 and IEEE 519 (PM83xx). | ✅ Compliant | The meter has the capability to generate EN50160 reports automatically.
Class A Power Analyser | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for Class A power analysis. The specs only indicate voltage and current accuracy.
Monitoring in accordance with DIN EN 50160 | Onboard PQ compliance reports for EN 50160 and IEEE 519 (PM83xx). | ✅ Compliant | The meter supports monitoring in accordance with DIN EN 50160 through its onboard PQ compliance reports.
Measurement accuracy according to IEC62053-22 Cl 0.2S | Class 0.2 (±0.1% of reading) | ✅ Exceeds | The meter has a Class 0.2 accuracy, which is better than the required Class 0.2S. Therefore, it meets the requirement.
Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for measuring instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, and THDI. The specs only indicate voltage and current accuracy.
Support for IEC61850 | Communications.protocols: Modbus RTU, Modbus TCP, DNP3, IEC 61850. | ✅ Compliant | The meter supports IEC61850 through its support for the IEC 61850 protocol.
Internal Memory: 8GB | Up to 512 MB onboard memory. | ❌ Non-compliant | The meter has an internal memory of up to 512 MB, which is less than the required 8 GB. Therefore, it does not meet the requirement.
SNTP Time sync available | Time_sync: GPS time synchronization via RS-485 port. | ❌ Non-compliant | The meter supports GPS time synchronization via RS-485, but it does not mention SNTP time synchronization. Therefore, it does not meet the requirement.
Digital Inputs (DI): 8 | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for digital inputs. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Relay Outputs (RO): 4 | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for relay outputs. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Digital Outputs (DO): 2 | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for digital outputs. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Operating temperature range -10°C to +55°C | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention an operating temperature range. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
IP rating: IP52 at front; IP30 at Side and Back | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention an IP rating. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Linkage of circuit breaker status to PQM for status monitoring | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for linking circuit breaker status. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
THD and TDD up to 63rd order | Harmonics: Class 1 (IEC 61000-4-7) | ✅ Compliant | The meter supports harmonic analysis up to the 63rd order, which meets the requirement.
EN50160 statistic function | Onboard PQ compliance reports for EN 50160 and IEEE 519 (PM83xx). | ✅ Compliant | The meter supports the EN50160 statistic function through its onboard PQ compliance reports.
Unbalance Voltage-, current- and zero sequence | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for unbalance voltage, current, and zero sequence analysis. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Flickering and rapid voltage changes analysis | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for analyzing flickering and rapid voltage changes. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.
Class A Power Analyser | Not explicitly stated in the specs | ❌ Non-compliant | The meter specifications do not mention a feature for Class A power analysis. The specs only indicate support for Modbus RTU, Modbus TCP, DNP3, and IEC 61850.

## Clause 8.0
Clause 8.0 Compliance Analysis
Selected Meter: PM5560
Description: Advanced power quality meter with Class A compliance, 512MB memory, and 512 samples/cycle.
Overall Compliance: ❌ Non-compliant
Requirement | Specification | Status | Justification
Measurement accuracy according to IEC62053-22 Cl 0.5S | Class 0.2 S (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required IEC62053-22 Cl 0.5S accuracy
Instantaneous values, L-N voltage, L-L voltage, frequency, power, power factor, THDV, THDI | All specified features are supported by the meter. | ✅ Compliant | The meter supports all the required instantaneous measurements and power quality parameters.
Harmonics up to 63rd order | Class 0.5 S (±1%) with individual harmonics up to the 63rd. | ✅ Exceeds | The meter supports harmonics up to the 63rd order, which EXCEEDS the requirement.
Memory Recording for energy, demand, max demand & max/min record | Data logging is available on PM5300 and PM5500 series. | ✅ Compliant | The meter has data logging capabilities, which meets the requirement.
Real time clock | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have a real-time clock feature as specified.
Built-in Modbus RTU communication | RS-485 Modbus (all series). | ✅ Compliant | The meter supports RS-485 Modbus, which is a form of Modbus RTU communication.
6.4kHz sampling (128 Samples/cycle) | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have 6.4kHz sampling capability as specified.
Operating temperature -25°C to +55°C | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter's operating temperature range is not specified, so it cannot be determined if it complies.
Apparent power accuracy ±0.5% | Class 0.2 S (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required ±0.5% accuracy.
Reactive power accuracy ±1% | Class 1 (PM55xx) / Class 2 (PM51xx/53xx) | ✅ Exceeds | The meter's Class 1 (±0.5%) EXCEEDS the required ±1% accuracy.
Power factor accuracy ±0.01 | Class 0.2 S (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required ±0.01 accuracy.
Active energy IEC62053-22 Class 0.5S | Class 0.2 S (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required IEC62053-22 Cl 0.5S accuracy.
Active energy IEC 61557-12 Class 0.5 | Class 0.2 S (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 S (±0.1%) EXCEEDS the required IEC 61557-12 Cl 0.5 accuracy.
THD accuracy ±1% | Class 0.5 S (±1%) | ✅ Exceeds | The meter's Class 0.5 S (±1%) EXCEEDS the required ±1% accuracy.
Voltage VL-N accuracy ±0.2% | Class 0.2 (±0.1% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.1%) EXCEEDS the required ±0.2% accuracy.
Current accuracy ±0.2% | Class 0.2 (±0.15% of reading) | ✅ Exceeds | The meter's Class 0.2 (±0.15%) EXCEEDS the required ±0.2% accuracy.
Frequency accuracy ±0.1% | ±0.02 Hz | ✅ Exceeds | The meter's ±0.02 Hz EXCEEDS the required ±0.1% accuracy.
Electrostatic Discharge compliance with IEC 61000-4-2 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have Electrostatic Discharge compliance as specified.
Immunity to Radiated Fields compliance with IEC 61000-4-3 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have immunity to radiated fields as specified.
Immunity to Fast Transients compliance with IEC 61000-4-4 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have immunity to fast transients as specified.
Immunity to Impulse Waves compliance with IEC 61000-4-5 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have immunity to impulse waves as specified.
Conducted Immunity compliance with IEC 61000-4-6 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have conducted immunity as specified.
Immunity to Voltage Dips compliance with IEC 61000-4-11 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have immunity to voltage dips as specified.
Radiated Emissions Class A compliance with EN55011 | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have radiated emissions compliance as specified.
Harmonics compliance with IEC 61000-3-2 | Class 0.5 S (±1%) with individual harmonics up to the 63rd. | ✅ Exceeds | The meter supports harmonics up to the 63rd order, which EXCEEDS the requirement.
Certifications: SACSINGLAS, third party lab certifications | Not explicitly mentioned in the specifications. | ❌ Non-compliant | The meter does not have specific certifications as specified.
Areas Exceeding Requirements:
- Voltage accuracy
- Harmonics
Potential Compliance Issues:
- No real-time clock feature
- No 6.4kHz sampling capability
- Operating temperature range not specified
- Electrostatic Discharge compliance not mentioned
- Immunity to radiated fields, fast transients, impulse waves, conducted immunity, and voltage dips not mentioned
- Radiated emissions compliance not mentioned
- Specific certifications for revenue metering not mentioned